specification sheet

th45

window ventilation - adjustable supply

manufacturer

RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium

tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be  www.renson.eu

series

NON-self-regulating

thermally broken

window ventilation

for installation on glass

types

TH45 for glass thickness 20 mm

TH45 for glass thickness 24 mm

TH45 for glass thickness 28 mm

description

The TH45 is a compact, non-self-regulating, thermally broken window ventilator.

The TH45 is designed for installation on glass (for glass thicknesses 20, 24, 28 mm) in PVC frames. A glazing gasket is recommended to guarantee a perfect fit.

The airflow is regulated by means of an aluminium flap on the inside. When open, it deflects the airflow upwards to prevent direct draughts.

Plastic foam on the inside of this flap seals the unit against water and wind when the flap is closed. Plastic clips in the aluminium flap ensure a tight fit against the PVC base section. Extra clips can be fitted or replaced later. The end caps are in white plastic.

The TH45 contains an aluminium plate with a series of 2.5 x 17.5 mm perforations to serve as an insect screen.

The extruded PVC base profile consists of one profile with 9.4 x 35 mm perforations to let the air through.

The TH45 is only available in white.

The unit can be controlled in various ways, including manual, rod or cord operation.

material & finish

Internal and external profile: PVC

Finish: white

Thermal bridge: PVC

End caps: ASA polymer type Luran S (colour-fast, weather- and UV-resistant)

End cap colours: white

dimensions

Glass reduction: 	45 mm

Height:			58 mm

Max. length: 		750 mm

control options

Manual operation, 2 stepped positions

Cord control, 2 stepped positions

Rod control, 2 stepped positions

Technical specifications

Airflow:

- Q at 1 Pa:		17,7 m³/h/m (4,9 l/s/m)

- Q at 2 Pa: 		25,0 m³/h/m (6,9 l/s/m)

- Equivalent Area:	6256 mm²/m

Sound reduction Dn,e,w (C;Ctr):

- Open:	27 (0;0) dB

- Closed: 	44 (0;0) dB

Self-regulation class: 	non-self-regulating: P0

U-value: 			n.p.d. W/m²K

Watertightness up to: 		350 Pa (closed)

Windtightness up to: 		350 Pa (closed)

standards

This product is manufactured according to, complies with and/or has been tested according to:

EN ISO 140-10

EN ISO 717-1

EN 1026

EN 1027

EN 13141-1

EN 12020-2

EN AW 6063 T66

NBN D50-001

EN 1077-2