**RENSON WINDOW VENTILATION® SPECIFICATIONS**

**Brand : AK80**

**Type : AK80GL**

**Manufacturer and reference:**

The AK80GL is manufactured and supplied by Renson Ventilation Tel: 01622 754 123 Email: [vents@rensonuk.net](mailto:vents@rensonuk.net)

**Description:**

The RENSON® AK80GL is a thermally broken, compact acoustic window ventilator for glazed-in installation. Perforations in the interior profile act as an insect mesh.

**System operation and performance:**

Thermal conductivity: U-value = 2.3 W/m2K (for AK80GL/4: 2.1 W/m2K).

Wind resistant: up to 650Pa in closed position.

Watertightness: up to 50Pa in open position and up to 650Pa in closed position.

**Airflow and Sound Reduction**:

**AK80GL/1 AK80GL /2 AK80GL /3 AK80GL /4**

Dn,e,w (C;Ctr) open (dB) 47 (0;-3) 44 (-1;-4) 41 (-1;-3) 33 (-1;-2)

Dn,e,w (C;Ctr) closed (dB) 51 (-1;-3) n.p.d n.p.d n.p.d

Q at 1 Pa (l/s/m ) 1,2 1,7 2,0 6,9

Q at 1 Pa (m³/h/m) 4,2 6,1 7,2 24,8

Q at 2 Pa (l/s/m ) 1,6 2,5 2,9 9,7

Q at 2 Pa (m³/h/m) 5,9 9,0 10,4 34,9

Q at 10 Pa (l/s/m) 3,6 5,8 7,1 21,1

Q at 20 Pa (l/s/m) 5,0 8,4 10,4 29,6

Equivalent area (mm²/m) 1488 2163 2545 8780

**Dimensions / Size Range:**

Height: 80 mm (total height with flanges: 123 mm)

Glass deduction: 108 mm

Maximum length: 2000mm (1250mm for cord control)

**Ventilator Construction:**

Profile: manufactured from aluminium alloy Al Mg Si 0.5.

Thermal bridge: PVC.

End caps: ASA polymer type Luran S (colour-fast, weather and UV-resistant).

Sound absorbing material: synthetic foam.

**Surface treatment:**

Satin anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (60 to 70 micron): aluminium profiles pre-treated to resist corrosion to guarantee. (bicolore possible)

End cap colours: white, black or grey (other colours available on request).

**Control options:**

Manual, cord, rod: 5 positions

Motorised: 24V DC

**Installation:**

Intended for installation at transom but can be mounted on glass (timber, uPVC or aluminium).

**Standards:**

EN ISO 140-10, EN ISO 717-1, EN 1026, EN 1027, EN 13141-1, EN 12020-2, EN AW 6063 T66, NBN D50-001, EN 1077-2.