RENSON LOUVRE SPECIFICATIONS

Brand		: LOUVRE

Type 		: 412 – BUILT-IN 20 mm pitch wall louvre

Manufacture and reference :

The 412 Louvre Panel is manufactured and supplied by Renson Fabrications Ltd. Tel: 01622 754123

Email: louvres@rensonuk.net Website: www.renson.eu

Description:

RENSON 412 is an extruded aluminium louvre panel which uses our V20 blade. It is designed to be built-in to a reveal and the chevron blades provide private ventilation which cannot be seen through from either side.

System operation and Airflow performance:

Type				412

Visual Free Area		93%

Physical Free Area		39%

K-factor: Intake			33.8

K-factor: Discharge		33.8

Ce coefficient: Intake		0.172

Cd coefficient: Discharge	0.172

Watertightness (HEVAC) – Class A (with water channel) at 0.5m/s

Dimensions/Size Range:

Minimum Dimensions (mm)	100 X 100

Flange Height (mm)		31

Depth (mm)			28.5

Pitch (mm)			20

Product Construction:

Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (40 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation:

To be built into a reveal. Bracket 418 included, spring clips 419 available on request. Reinforcing structure needed on panels larger than 3m2.

Accessories

Stainless steel birdguard 6mm x 6mm secured to the rear

Stainless steel insect mesh 2.3mm x 2.3mm secured to the rear

Backframe, pre-installation frame, water channel, drainage channel

Circular louvre type 412R

Product Information:

http://www.rensonuk.net/Louvres-panels-United-Kingdom.html