## Specifications sheet

469 INVISIDO®
DOOR LOUVRE - TRANSIT VENT

MANUFACTURER
RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium
tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be www.renson.eu

SERIES
AESTHETIC
DOOR LOUVRE
FOR INSTALLATION ABOVE DOOR

TYPES
469

DESCRIPTION
The discreet 469 Invisido® door louvre is a two-piece unit for installation above the door.

The 469 Invisido® consists of extruded aluminium sections that are screwed in place above the door panel and under the door frame, across the whole width of the panel and frame.

The door panel is shortened or milled as shown in the assembly instructions. The predrilled holes in the 469 Invisido® make it quick to attach to the door panel and frame. A sound-absorbing foam hides the screws.

The units come in standard sizes to fit 730 mm, 830 mm and 930 mm doors; other sizes are available upon request.

The frame sections can be satin anodised or powder-coated (any RAL colour). 
End caps for the frame sections come in standard colours of white, cream, black or grey (depending on the colour of the frame), but other colours are also possible upon request. 

Thanks to the unit’s special shape, it is virtually impossible to see from one room to the other (depending on how it is installed).

The 469 Invisido® is suitable only for internal doors and guarantees a flow of air between rooms.

The 469 Invisido® is easy to clean using a brush or vacuum cleaner.

MATERIAL & FINISH
Frame: AlMgSi 0.5 aluminium (according to EN 12020-2 and EN AW-6063)
Finish: satin anodised (SAA) (20 micron) or powder-coated (60-70 micron) in any RAL colour
End caps: Luran S ASA polymer (colour-fast, weather- and UV-resistant)
End cap colours: white, cream, black, grey, other colours upon request
Sound-reducing material: absorbent plastic foam

DIMENSIONS
Frame width : 30 mm
Frame height : 13 mm
Standard lengths : 730 mm, 830 mm, 930 mm
Minimum length : 500 mm
Maximum length : 2,000 mm

INSTALLATION
In accordance with installation instructions, using screws suitable for the base material (the supplied screws may not be suitable).
Note: The installation can vary, depending on door thickness, door width and the desired flow rate.

OPTIONAL EXTRAS
None

TECHNICAL SPECIFICATIONS
469 INVISIDO® 830 MM STANDARD INSTALLATION
Airflow: 
- Q at 1 Pa: 17.9 m³/h/m (5.0 dm³/s/m)
- Q at 2 Pa: 25.1 m³/h/m (7.0 dm³/s/m)
- Q at 10 Pa: 55.2 m³/h/m (15.3 dm³/s/m)
- Q at 20 Pa: 77.6 m³/h/m (21.6 dm³/s/m)

Sound reduction Dn,e,w (C;Ctr): 28 (-1;0) dB

STANDARDS
This product is manufactured according to, complies with and/or has been tested according to:
EN 13141-1
EN ISO 140-10
EN ISO 717-1
EN 12020-2
EN AW 6063 T66
NBN D50-001
NEN 1087