RENSON LOUVRE SPECIFICATIONS

Brand		: LOUVRE PANEL

Type 		: 432 – SURFACE MOUNTED 33mm pitch louvre

Manufacture and reference :

The 432 Louvre Panel is manufactured and supplied by Renson Fabrication Ltd.  Tel: 01622 754123

Email: louvres@rensonuk.net Website: www.renson.eu

Description:

RENSON 432 is an extruded aluminium louvre panel using a L.033 pitch blade mounted into an integrated frame. It is designed to be surface mounted onto a fixed structure, including some window frames.

System operation and Airflow Performance:

Type				432

Visual Free Area		59%

Physical Free Area		45%

K-factor: Intake			23.6

K-factor: Discharge		25.5

Ce coefficient: Intake		0.206

Cd coefficient: Discharg	e	0.198

Dimensions/Size Range:

Minimum Dimensions (mm)	136 x 136

Thickness (mm)		40

Pitch (mm)			33

Product Construction:

Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (40 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation:

Surface mounted using the screws and plugs that are provided.

Accessories

Stainless steel birdguard 6mm x 6mm secured to the rear

Stainless steel insect mesh 2.3mm x 2.3mm secured to the rear

Product Information:

http://www.rensonuk.net/Louvres-panels-United-Kingdom.html