RENSON LOUVRE SPECIFICATIONS

Brand		: LOUVRE PANEL

Type 		: 480 – BUILT-IN 60mm pitch wall louvre

Manufacture and reference :

The 480 Louvre Panel is manufactured and supplied by Renson Fabrication Ltd.  Tel: 01622 754123

Email: louvres@rensonuk.net Website: www.renson.eu

Description:

RENSON 480 is a heavy duty extruded aluminium louvre panel using a L.060HF pitch blade mounted into an integrated frame. It is designed to be built into a pre formed opening. It can be supplied with or without a flanged frame.

System operation and Airflow Performance:

Type				480

Visual Free Area		90%

Physical Free Area		76%

K-factor: Intake			5.03

K-factor: Discharge		4.96

Ce coefficient: Intake		0.446

Cd coefficient: Discharge	0.449

Dimensions/Size Range:

Minimum Dimensions (mm)	300 x 300

Flange Height (mm)		50

Depth (mm)			81.5

Pitch (mm)			60

Product Construction:

Profile: Extruded aluminium (EN 12020-2)

Surface Treatment:

Mill finish

Anodised (EV6/EV1) (20 micron): pre-treated and anodised.

Polyester powder coating in any RAL colour (40 micron): aluminium profiles pre-treated to resist corrosion to guarantee.

Installation:

To be built into a reveal. Bracket 429 included on request. Reinforcing structure needed on panels larger than 3m2

Accessories

Stainless steel birdguard 6mm x 6mm secured to the rear

Stainless steel insect mesh 2.3mm x 2.3mm secured to the rear

Backframe, pre-installation frame, water channel, drainage channel

Product Information:

http://www.rensonuk.net/Louvres-panels-United-Kingdom.html