## Specifications sheet

MANUFACTURER
RENSON Ventilation, IZ 2 Vijverdam, Maalbeekstraat 10, 8790 Waregem – Belgium
tel. +32 (0)56 62 71 11, fax. +32 (0)56 60 28 51, info@renson.be www.renson.eu

SERIES
BUILT-IN
WALL LOUVRE 
WITH CHEVRON SECTION BLADES 

TYPES
452

DESCRIPTION
The 452 louvre is a built-in wall louvre with large chevron section V-blades and excellent watertightness (class A, up to 1.0 m/s according to EN13030).

Extruded, L-shape, aluminium frame profiles with a total height of 64 mm are cut at mitre of 45° and assembled through compression and a clamping corner.

Aluminium blade supports are pop-riveted to the perforated vertical frame profiles.
Louvres with a width over 700 mm are provided with an extra perforated U-profile to fit supplementary blade supports for reinforcement.

The extruded aluminium blades are clipped into the blade supports. The distance between the blades is 66 mm. The blades are V-shaped, allowing no see-through visibility. 

An anti-static 304 stainless steel 6 x 6 mm mesh wire is tensioned tight inside the frame using a nylon wire.

The finish can be anodised (natural) or powder-coated (any RAL colour). 

Minimum dimensions are 305 x 305 mm (WxH) 
For larger sizes, multiple 452 louvres may be linked together on request.

The louvre is optionally available with a frame without flange.
A version for installation in window frames is also available on request.

MATERIAL & FINISH
Blades and frame profile: aluminium AlMgSi 0.5 (according to EN 12020-2 and EN AW-6063)
Finish: natural (SAA) anodised (20 micron) or powder-coated (60-70 micron) in any RAL colour 
Mesh: standard anti-static 304 stainless steel 6 x 6 mm mesh wire, tensioned tight inside the frame using a nylon wire.
Note: louvres with a width over 700 mm are provided with an extra perforated strengthening U-profile to fit supplementary blade supports for reinforcement.

DIMENSIONS
Depth to fit : 81.5 mm
Blade pitch : 66 mm
Flange size : 50 mm
Total thickness : 86.5 mm
Minimum dimensions : 305 mm x 305 mm (W x H)
Maximum dimensions : on request (W X H)

INSTALLATION
Should be installed in accordance with installation instructions, using plugs and screws as appropriate for the wall and/or surface material (not included in the delivery).
Wall brackets nr. 429 for securing against the wall are included in the delivery.
Note: A reinforcing backstructure is required for louvres of more than 3m2.

OPTIONAL EXTRAS
- Water channel: installed under the lowest blade; provides enhanced water drainage. This water channel is made of aluminium AlMgSi 0.5, anodized and powder-coated in the same finish as the louvre.
- Insect mesh: anti-static, 304 stainless steel 2.3 x 2.3 mm insect mesh or 10 x 10 mm bird mesh.
- Removable insect mesh: anti-static, 304 stainless steel 2.3 x 2.3 mm insect mesh / 6 x 6 mm wire mesh / 10 x 10 mm bird mesh with integrated water channel.

TECHNICAL SPECIFICATIONS
452
Airflow: 
- K-factor, supply: 66,1
- K-factor, extraction: 79,7
- Ce coefficient: 0,123
- Cd coefficient: 0,112

Free area:
- Visual free area 70%
- Physical fee area 41%

Protection:
- IP class: 2XD
- HEVAC-class 0.0m/s: A 
- HEVAC-class 0.5m/s: A 
- HEVAC-class 1.0m/s: A 
- HEVAC-class 1.5m/s: B 
- HEVAC-class 2.0m/s: D
- Resistance class: n.p.d.

Sound reduction Rw (C;Ctr): 
- Open: n/a 

STANDARDS
This product is manufactured according to, complies with and/or has been tested according to:
EN ISO 140-10
EN ISO 717-1
EN 12020-2
EN AW 6063 T66
EN 13030
EN 60529